## Results
Single Phase 240-120 Volt System Line Current Calculator | [9 empty] | Reference Dataforth AN109
Place Curser for Instructions: | [8 empty] | System Power Triangle
Reference
[15 empty] | Real | j Img
System Volts | [6 empty] | System Results | [5 empty] | Totals | I1 | 114.606 | -80.1104
Line to Line |  | 240 |  | Item | I1 | I2 | In | P | Q | VA | PF |  | Totals | I2 | -100.4214 | 81.811
Line to Neutral |  | 120 |  | Units | A rms | A rms | A rms | KW | KVAR | KVA | none |  | Totals | In | 14.1846 | 1.7005
|  |  |  | Value | 139.8293 | 129.528 | 14.2862 | 25.8033 | 19.4306 | 32.301 | 0.79884
|  |  |  | Angle° | -34.9538 | 140.8311 | 6.8363 | 0 | 90 | 36.9807 | LAG
L1-L2 Loads |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  |  |  | I1 |  | I2
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle° | RMS | Angle° |  |  | Real | j Img | Real | j Img
1 | KW |  | 3 |  | 100 | 1 |  | 12.5 | 0 | 12.5 | 180 |  |  | 12.5 | 0 | -12.5 | 1.5314e-15
2 | KVA |  |  | 10 |  | 0.1 | L | 41.6667 | -84.2608 | 41.6667 | 95.7392 |  |  | 4.1667 | -41.4578 | -4.1667 | 41.4578
3 | Motor | 7 |  |  | 95 | 0.8 | L | 28.6294 | -36.8699 | 28.6294 | 143.1301 |  |  | 22.9035 | -17.1776 | -22.9035 | 17.1776
4 | [7 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5 | [7 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | Totals | 70.7383 | -55.9865 | 70.7383 | 124.0135 |  | Totals | 39.5702 | -58.6354 | -39.5702 | 58.6354
L1-N Loads |  | Output |  | Input | EFF | PF |  | I1 phasor | [5 empty] | I1 |  | I2
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle° |  |  |  |  | Real | j Img | Real | j Img
1 | KW |  | 5 |  | 100 |  |  | 41.6667 | 0 |  |  |  |  | 41.6667 | 0
2 | KVA |  |  | 3 |  | 0.8 | L | 25 | -36.8699 |  |  |  |  | 20 | -15
3 | Motor | 2 |  |  | 93 | 0.9 | L | 14.8546 | -25.8419 |  |  |  |  | 13.3692 | -6.475
4 | [7 empty] | 0 | 0 |  |  |  |  | 0 | 0
5 | [7 empty] | 0 | 0 |  |  |  |  | 0 | 0
[7 empty] | Totals | 78.0484 | -15.9709 |  |  |  | Totals | 75.0358 | -21.475
L2-N Loads |  | Output |  | Input | EFF | PF |  |  |  | I2 phasor |  |  |  | I1 |  | I2
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C |  |  | RMS | Angle° |  |  | Real | j Img | Real | j Img
1 | KW |  | 2 |  | 100 |  |  |  |  | 16.6667 | 180 |  |  |  |  | -16.6667 | 2.0419e-15
2 | KVA |  |  | 5 |  | 0.9 | L |  |  | 41.6667 | 154.1581 |  |  |  |  | -37.5 | 18.1621
3 | Motor | 1 |  |  | 93 | 0.8 | L |  |  | 8.3557 | 143.1301 |  |  |  |  | -6.6846 | 5.0134
4 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0
5 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0
[9 empty] | Totals | 65.1151 | 159.1504 |  | Totals |  |  | -60.8513 | 23.1755
Note on H28: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on C22: Enter System Voltage V12, Line to Line
Note on H38: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on H48: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on G8: 1. Voltage L1 to L2 (V12) is Defined as Reference 2. All Angles Measured Counterclock Wise from Reference V12. 3. Current Directions Assumed as Shown in Figure 4. Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF 5. Load Power Factor Angles, Referenced to Reference Voltage V12 6. Enter Power Factor Values with; a) “L” for Lagging Inductive Loads b) “C” for Leading Capacitive Loads 7. Place curser on cells containing comments for more instructions.
Note on C28: Motor Load: Enter; HP, EFF, PF
Note on E28: KVA Load: Enter; KVA, PF
Note on D28: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on B38: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on B48: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on B28: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on L22: If Angle of Power Triangle angle is: (a) positive, circuit is inductive with Lagging Power factor (b) negative, circuit is capacitive with Leading Power Factor
Note on J22: Positive Q = Lagging Inductive Circuit Negative Q = Leading Capactive Circuit
Note on L27: The direction of I1 is into the load; therefore, I2 is out of load I2 = -I1.
Note on C38: Motor Load: Enter; HP, EFF, PF
Note on D38: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E38: KVA Load: Enter; KVA, PF
Note on C48: Motor Load: Enter; HP, EFF, PF
Note on D48: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E48: KVA Load: Enter; KVA, PF