## System Defined
Line Current Calculator for Three Phase Systems See Dataforth AN110 for Reference
Three-Phase 4-wire Wye System with; |  |  |  | Place Curser for Information-Instructions:
1. Individual single-phase line-to-neutral loads
2. Individual single-phase line-to-line loads |  |  |  |  | System Calculation Results: Sequence {1 2 3} V12 at zero degrees
3. Individual balanced 3-phase wye loads |  |  |  |  | Item | I1 | I2 | I3 | In | P | Q | VA | PF
4. Individual balanced 3-phase delta loads. |  |  |  |  | Units | A rms | A rms | A rms | A rms | KW | KVAR | KVA | none
[5 empty] | Value | 320.6043 | 324.8581 | 389.0916 | 89.5505 | 118.6673 | 36.2869 | 124.0914 | 0.95629
[5 empty] | Angle° | -43.1938 | -167.2359 | 70.0539 | 56.3379 | 0 | 90 | 17.0029 | LAG
Single Phase
Line-to Neutral Loads
Defines an unbalanced
3-Phase Wye System
Individual Single Phase
Line-to-Line Loads
Defines an unbalanced
3-Phase Delta System
Balanced 3-Phase Loads
Wye Delta
| Total System Power Triangle |  |  |  |  | Three-Phase Voltage Vector System
Line Voltage V12 Chosen as Reference
Note on S8: 1. Phase Sequence Chosen as {1 2 3} 2. V12 = Line-to-Line volts at 0 degrees Defined as Reference 3. V23 = Line-to-Line volts at -120 degrees 4. V31 = Line-to-Line volts at 120 degrees 5. V1N = Line-to-Neutral volts at -30 degrees 6. V2N = Line-to-Neutral volts volts at -150 degrees 7. V3N = Line-to-Neutral volts volts at 90 degrees 8. All Angles Measured Counterclock Wise from Reference V12 Example, -60 degrees = 300 degrees. 9. Current Directions Assumed as Shown 10. Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF, c) Motor Load: Enter; HP, EFF, PF 11. Must Enter Power Factor (PF) Values with either; a) “L” for Lagging Inductive Loads or b) “C” for Leading Capacitive Loads NOTE: To Remove Loads, delete the " load type" information in the "Type" column cells . Deleting only the load data causes calculation errors. 12. Current Angles measured wrt reference Voltage V12 13. Place curser on cells containing comments for information review

## Calculations
3-Phase System Volts
Line to Line |  | 208 |  | Line to Neutral | 120.0889
3-Phase Wye |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-wye | I1 3-Phase Balanced Wye |  |  | I2 3-Phase Balanced Wye |  |  | I3 3-Phase Balanced Wye
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 16455.7774 | Real | jImg |  | Real | jImg |  | Real | jImg
1 | kw |  | 7 |  | 95 |  |  | 20.4527 | -30 | 20.4527 | -150 | 20.4527 | 90 | Q-wye | 17.7126 | -10.2263 |  | -17.7126 | -10.2263 |  | 1.2529e-15 | 20.4527
2 | kva |  |  | 6 |  | 0.8 | L | 16.6543 | -66.8699 | 16.6543 | -186.8699 | 16.6543 | 53.1301 | 5676.4614 | 6.5422 | -15.3156 |  | -16.5348 | 1.9921 |  | 9.9926 | 13.3235
3 | motor | 5 |  |  | 87 | 0.9 | L | 13.2228 | -55.8419 | 13.2228 | -175.8419 | 13.2228 | 64.1581 | (VI*)3^0.5 | 7.4243 | -10.9417 |  | -13.188 | -0.95876 |  | 5.7637 | 11.9005
[7 empty] | Totals | 48.3179 | -49.032 | 48.3179 | -169.032 | 48.3179 | 70.968 | Totals | 31.679 | -36.4837 | Totals | -47.4353 | -9.193 | Totals | 15.7563 | 45.6767
[14 empty] | R, X = 0 Test | FALSE
3-Phase Delta |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-Delta | I1 3-Phase Balanced Delta |  |  | I2 3-Phase Balanced Delta |  |  | I3 3-Phase Balanced Delta
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 19248.3516 | Real | jImg |  | Real | jImg |  | Real | jImg
1 | kw |  | 3.5 |  | 100 |  |  | 9.715 | -30 | 9.715 | -150 | 9.715 | 90 | Q-Delta | 8.4135 | -4.8575 |  | -8.4135 | -4.8575 |  | 5.9512e-16 | 9.715
2 | kva |  |  | 10 |  | 0.96 | C | 27.7572 | -13.7398 | 27.7572 | -133.7398 | 27.7572 | 106.2602 | -180.8132 | 26.9629 | -6.5927 |  | -19.1909 | -20.0542 |  | -7.772 | 26.6469
3 | motor | 7.5 |  |  | 91 | 0.92 | L | 18.5501 | -53.0739 | 18.5501 | -173.0739 | 18.5501 | 66.9261 | (VI*)3^0.5 | 11.1446 | -14.8292 |  | -18.4148 | -2.2369 |  | 7.2701 | 17.0661
[7 empty] | Totals | 53.4304 | -29.4618 | 53.4304 | -149.4618 | 53.4304 | 90.5382 | Totals | 46.521 | -26.2794 | Totals | -46.0191 | -27.1487 | Totals | -0.50189 | 53.4281
[14 empty] | R, X = 0 Test | FALSE
L1-N Loads |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-1N | I1-N Single Phase 120-volt
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 11543.043 | Real | jImg
1 | kw |  | 5 |  | 95 |  |  | 43.8272 | -30 |  |  |  |  | Q-1N | 37.9555 | -21.9136
2 | kva |  |  | 3 |  | 0.95 | L | 24.9815 | -48.1949 |  |  |  |  | 2597.9189 | 16.6526 | -18.6216
3 | motor | 4 |  |  | 87 | 0.9 | L | 31.7347 | -55.8419 |  |  |  |  | (VI*) | 17.8183 | -26.2602
[7 empty] | Totals | 98.5252 | -42.6839 |  |  |  |  | I1N Totals | 72.4264 | -66.7954
[14 empty] | R, X = 0 Test | FALSE
L2-N Loads |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-2N | I2-N Single Phase 120-volt
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 9848.2759 | Real | jImg
1 | kw |  | 3 |  | 90 |  |  |  |  | 27.7572 | -150 |  |  | Q-2N | -24.0385 | -13.8786
2 | kva |  |  | 6 |  | 0.8 | L |  |  | 49.963 | -186.8699 |  |  | 4430.5846 | -49.6043 | 5.9763
3 | motor | 2 |  |  | 87 | 0.9 | L |  |  | 15.8673 | -175.8419 |  |  | (VI*) | -15.8256 | -1.1505
[7 empty] | Totals |  |  | 89.9252 | -174.2222 |  |  | I2N Totals | -89.4683 | -9.0528
[14 empty] | R, X = 0 Test | FALSE
L3-N Loads |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-3N | I3-N Single Phase 120-volt
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 18059.3189 | Real | jImg
1 | kw |  | 6 |  | 95 | [6 empty] | 52.5926 | 90 | Q-3N | 3.2217e-15 | 52.5926
2 | kva |  |  | 7 |  | 0.8 | L |  |  |  |  | 58.2902 | 53.1301 | 8007.4176 | 34.9741 | 46.6321
3 | motor | 7 |  |  | 85 | 0.85 | L |  |  |  |  | 60.1861 | 58.2117 | (VI*) | 31.705 | 51.1582
[7 empty] | Totals |  |  |  |  | 164.5027 | 66.0877 | I3N Totals | 66.6791 | 150.383
[14 empty] | R, X = 0 Test | FALSE
L1-L2 Loads |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-12 | I12 Single Phase 208-volt
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 14479.8851 | Real | jImg
1 | kw |  | 5 |  | 80 |  |  | 30.0481 | 0 | 30.0481 | 180 |  |  | Q-12 | 30.0481 | 0
2 | kva |  |  | 6 |  | 0.8 | L | 28.8462 | -36.8699 | 28.8462 | 143.1301 |  |  | 5261.1692 | 23.0769 | -17.3077
3 | motor | 4 |  |  | 87 | 0.9 | L | 18.322 | -25.8419 | 18.322 | 154.1581 |  |  | (VI*) | 16.4898 | -7.9864
[7 empty] | Totals | 74.0676 | -19.9683 | 74.0676 | 160.0317 |  |  | I12 Totals | 69.6148 | -25.2941
[14 empty] | R, X = 0 Test | FALSE
L2-L3 Loads |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-23 | I23 Single Phase 208-volt
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 15994.4444 | Real | jImg
1 | kw |  | 5 |  | 80 |  |  |  |  | 30.0481 | -120 | 30.0481 | 60 | Q-23 | -15.024 | -26.0224
2 | kva |  |  | 7 |  | 0.8 | L |  |  | 33.6538 | -156.8699 | 33.6538 | 23.1301 | 6207.2461 | -30.9486 | -13.2199
3 | motor | 5 |  |  | 90 | 0.9 | L |  |  | 22.1391 | -145.8419 | 22.1391 | 34.1581 | (VI*) | -18.3199 | -12.4306
[7 empty] | Totals |  |  | 82.4841 | -141.2106 | 82.4841 | 38.7894 | I23 Totals | -64.2926 | -51.6729
[14 empty] | R, X = 0 Test | FALSE
L3-L1 Loads |  | Output |  | Input | EFF | PF |  | I1 phasor |  | I2 phasor |  | I3 phasor |  | P-31 | I3I Single Phase 208-volt
Load # | Type | HP | KW | KVA | % | 0 to 1 | I or C | RMS | Angle | RMS | Angle | RMS | Angle | 13038.2353 | Real | jImg
1 | kw |  | 5 |  | 80 |  |  | 30.0481 | 300 |  |  | 30.0481 | 120 | Q-31 | -15.024 | 26.0224
2 | kva |  |  | 3 |  | 0.8 | L | 14.4231 | 263.1301 |  |  | 14.4231 | 83.1301 | 4286.9275 | 1.7252 | 14.3195
3 | motor | 5 |  |  | 85 | 0.87 | L | 24.2498 | 270.4586 |  |  | 24.2498 | 90.4586 |  | -0.19411 | 24.249
[7 empty] | Totals | 65.9852 | 281.7993 |  |  | 65.9852 | 101.7993 | I31 Totals | -13.4929 | 64.5909
[14 empty] | R, X = 0 Test | FALSE
Line Currents for Unbalanced Line-Line Delta Loads
[15 empty] | Real | jImg
[14 empty] | I1=I12- I31 | 83.1078 | -89.885 | I1=I12+ I13
[14 empty] | I2=I23- I12 | -133.9074 | -26.3789 | I2=I23+ I21
[14 empty] | I3=I31- I23 | 50.7996 | 116.2638 | I3=I31+ I32
[14 empty] | IN=0 check | 0 | 0 | I1+ I2 + I3
System Total Line Currents
[15 empty] | Real | jImg | Mag | Angle | R,X = 0 Test
[14 empty] | I1 | 233.7342 | -219.4435 | 320.6043 | -43.1938 | FALSE
[14 empty] | I2 | -316.8302 | -71.7733 | 324.8581 | -167.2359 | FALSE
[14 empty] | I3 | 132.7331 | 365.7516 | 389.0916 | 70.0539 | FALSE
[14 empty] | IN | 49.6372 | 74.5348 | 89.5505 | 56.3379 | FALSE
System Results
[14 empty] | Item | I1 | I2 | I3 | In | P | Q | VA | PF
[14 empty] | Units | A rms | A rms | Arms | A rms | KW | KVAR | KVA | none
[14 empty] | Value | 320.6043 | 324.8581 | 389.0916 | 89.5505 | 118.6673 | 36.2869 | 124.0914 | 0.95629
[14 empty] | Angle° | -43.1938 | -167.2359 | 70.0539 | 56.3379 | 0 | 90 | 17.0029 | LAG
[20 empty] | R,X = 0 Test | FALSE
Note on B6: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C6: Motor Load: Enter; HP, EFF, PF
Note on D6: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E6: KVA Load: Enter; KVA, PF
Note on H6: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on B13: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C13: Motor Load: Enter; HP, EFF, PF
Note on D13: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E13: KVA Load: Enter; KVA, PF
Note on H13: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on B20: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C20: Motor Load: Enter; HP, EFF, PF
Note on D20: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E20: KVA Load: Enter; KVA, PF
Note on H20: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on B27: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C27: Motor Load: Enter; HP, EFF, PF
Note on D27: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E27: KVA Load: Enter; KVA, PF
Note on H27: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on B34: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C34: Motor Load: Enter; HP, EFF, PF
Note on D34: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E34: KVA Load: Enter; KVA, PF
Note on H34: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on B41: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C41: Motor Load: Enter; HP, EFF, PF
Note on D41: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E41: KVA Load: Enter; KVA, PF
Note on H41: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on B48: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C48: Motor Load: Enter; HP, EFF, PF
Note on D48: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E48: KVA Load: Enter; KVA, PF
Note on H48: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on B55: Enter Load Type Information from Name Plate Data a) KW Load: Enter; KW, EFF b) KVA Load: Enter; KVA, PF c) Motor Load: Enter; HP, EFF, PF
Note on C55: Motor Load: Enter; HP, EFF, PF
Note on D55: KW Load: Enter; KW, EFF Note: Some KW output loads may not have EFF specified, user may choose any reasonable value
Note on E55: KVA Load: Enter; KVA, PF
Note on H55: “L” for lagging Inductive loads "C” for leading Capacitive loads
Note on C3: Enter System Voltage V12, Line to Line
Note on B19: For 3-phase 3-wire Delta systems, enter "zero" for load data
Note on B26: For 3-phase 3-wire Delta systems, enter "zero" for load data
Note on B33: For 3-phase 3-wire Delta systems, enter "zero" for load data